## Slide 1: Single phase active filter for harmonic compensation
By
Ashok Saini
(Roll no. 24M1353)
Aditya Kumar
(Roll no. 24M1355)
M.Tech (1st year)
Subject – EN662
Under the guidance of
Prof. D. Venkatramanan
Department of Energy Science and Engineering
Indian Institute of Technology Bombay, Powai, 400076
May 2025

## Slide 2: Problem statement
In 1-phase power systems,
Non-linear and reactive loads – Harmonic currents and reactive power
Conventionally, passive L-C filters were used.
But
Solution ?
Large size
Fixed compensation
Resonance
Weight
Noise
Losses
Active power filter

## Slide 3: Introduction
Examples of non-linear loads – Variable speed drives, temperature controllers, electric furnaces, light controllers, solid state ac voltage regulators, SMPS and UPS.
Concern ?
Power quality issues,
Low efficiency of supply system
Poor power-factor
Destruction of other equipments due to excessive stresses
EMI problems
Active power filters (APF) – first introduced by Gyugi and Strycula.
APF connected in shunt mode with load through a filtering inductor.

## Slide 4: Power circuit Architecture
Fig 1 - Basic circuit of the Active power filter
https://doi.org/10.1109/PQ.1998.710359

## Slide 5: Control scheme
PI controller
Reference current generator
Current controller
Unit vector generator
APF
Vr
Vdc
Ism*
is*
is
4 Gating signals
Vs
u(t)
Fig 2 - Control scheme of the APF
https://doi.org/10.1109/PQ.1998.710359

## Slide 6: Analysis and model equations
A. Voltage controller
Ve(n) = Vr(n) - Vdc(n)
Vo(n) = Vo(n-1) + Kp{Ve(n) – Ve(n-1)} + Ki Ve(n)
where
Vdc = DC bus capacitor voltage
Vr = Set reference voltage
Ve(n) = Voltage error at nth sample instant
Vo(n) = Output of PI voltage controller
B. Reference current generation
u(t) = vs/Vsm = sinωt
is*(t) = Ism*u(t) = Ism*sinωt
where
Vsm = Peak value of supply voltage
Ism*(t) = Peak estimated value of supply current
is* = Reference source current

## Slide 7: Analysis and model equations
C. Current controller
The carrierless PWM hysteresis current controller contributes to switching pattern of the APF devices.
va = Vdc(SA – SB)
where
SA = 1 ; S1 ON
SA = 0 ; S2 ON
SB = 1 ; S3 ON
SB = 0 ; S4 ON
D. Active power filter
AC side -
Rc ic + + va = vs
= {vs – va – Rc ic}/Lc
DC side -
= idc / ic
idc = ic (SA – SB)
where
Va = APF voltage
Rc and Lc = APF resistor and inductance

## Slide 8: Analysis and model equations
E. Rectifier with capacitive loading
RSLiL + LSLdiL/dt + vL = vS
PiL = (vS – vL – RSLiL)/LSL
dvL/dt = (id – iR)/CL
where
RSL and LSL = Source impedance elements
id = Magnitude of iL
iR = Resistive DC load current
CL = Load capacitor
vL = voltage across load capacitor CL

## Slide 9: Circuit diagram with Active power filter
Fig 3 – Circuit diagram

## Slide 10: Control Architecture
Fig 4 – Control diagram

## Slide 11: Waveforms
Fig 5 - Source current with THD (%)

## Slide 12: Waveforms
Fig 7 - Filter current with THD (%)

## Slide 13: Design details
Supply : Vs(rms) = 220 V, f = 50 Hz,
Filter data : Rc = 0 ohm,
Lc = 4 mH,
Cc = 50 microF,
Series impedance : RSL = 0.5 ohm,
LSL = 1 mH,
Controller data : KP = 0.45, Ki = 1
Load : RL = 10 CL = 10 microF

## Slide 14: Conclusion
A simple and effective design of single-phase Active Power Filter (APF) is studied .
The APF uses:
A VSI with hysteresis current control
A PI-controlled DC bus with a small energy storage capacitor
Successfully compensated the harmonic currents
Simulation results show:
Reduced source current distortion
Enhanced supply system performance
It can further be extended for Grid connected PV systems also. (Already been implemented)

## Slide 15: References
B. Singh, K. Al-Haddad and A. Chandra, "A universal active power filter for single-phase reactive power and harmonic compensation," Power Quality '98, Hyderabad, India, 1998.
J. R. Mattar, J. C. Strutz, R. Hausmann, S. V. G. Oliveira and A. Péres, "A single phase active filter as a harmonic compensator," 2013 Brazilian Power Electronics Conference, Gramado, Brazil, 2013.
B. L. Cortes, M. S. Horta, S. A. Claudio and G. V. M. Cardenas, "Single-phase active power filter for reactive power and harmonic compensation," 6th IEEE Power Electronics Congress. Technical Proceedings. CIEP 98 (Cat. No.98TH8375), Morelia, Mexico, 1998.